## piping-class-a10-component-item
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE, Galvanized | A106 GR. B | 49
| 2 - 10 | Seamless, BE | A106 GR. B | 49
Fittings | 1/2 - 1 1/2 | Class 3000 SW, Galvanized | A105N | 49, 49
| 2 - 10 | BW Fittings, SCH 40 | A234 WPB | 49
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 THD Ends, Galvanized | A106 GR. B | 49
Swages | 1/2 - 2 | Bore to match pipe, THD, Galvanized | A234 WPB | 49
Flanges | 1/2 - 1 1/2 | Class 150 RF THD, Galvanized | A105N
| 2 - 10 | Class 150 RFWN, SCH 40 | A105N | 49
Bolting | All | Studs | A193 GR. B7
|  | Nuts | A194 GR. 2H
Gaskets | All | Class 150 - 3 mm THK Ring Gasket "Klingrite 1000", Durlon 8600" or "Garlock 3100" or Owner approved equivalent | 316/SS
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD | GA-808
| 2 - 6, 8 - 10 | Class 150 Flanged | GA-100/101
GLOBE
| 3/4 - 1 1/2 | Class 800 THD | GL-808
| 2 - 4 | Class 150 Flanged | GL-100
CHECK
| 3/4 - 1 1/2 | Class 800 THD, Lift-type | CH-808
| 2 - 10 | Class 150 Flanged Swing type | CH-100
BALL
| 3/4 - 1 1/2 | Class 800 THD | BA-808 | 5
| 2 - 6, 8 - 10 | Class 150 Flanged | BA-100/101 | 5
Caption: Piping Class A10 component items
Extracted from 03-piping-materials-and-line-classes-04 page 16, table 2.