## class-a13-piping-materials
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, PE | A106 GR. B
| 2 - 36 | Seamless, BE | A106 GR. B | 18, 42, 48
Fittings | 1/2 - 1 1/2 | Class 3000 SW, THD | A105N
| 2 - 10 | Butt Welded, WT to match pipe. | A234 WPB
| 12 - 36 | Fab. Same material as pipe. |  | 40
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 Minimum | A106 GR. B
Swages | 1/2 - 2 | Bore to match pipe | A234 WPB
Flanges | 1/2 - 1 1/2 | Class 150, RFSW, THD | A105N
| 2 - 24 | Class 150 RFFWN, bore to match pipe. | A105N | 2
| 36 & Over | Class 150 RFSO, ANSI B16.47, Series B (Special) | A105N | 2
Bolting | All | Studs | A193 GR. B7M
|  | Nuts | A194 GR. 2HM
Gaskets | 1/2 - 18 | Class 150 - 3 mm (1/8") THK Ring Gasket, "Klingserite 1000", "Durlon 8600" or "Garlock 3100" or Owner approved equivalent
| 20 - 36 | Double Jacketed Mild Steel 3 mm (1/8") THK.
Valves | GATE:
| 1/2 - 1 1/2 | Class 800 SW X TH | GA-807
| 1/2 - 1 1/2 | Class 800 THD | GA-808
| 1/2 - 1 1/2 | Class 800 SW | GA-806
Caption: CLASS A13 — Piping Materials
Extracted from 03-piping-materials-and-line-classes-04 page 19, table 2.