## class-a15-piping-components
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | All in accordance with Pipe Class A
Fittings | 1/2 - 1 1/2 | All in accordance with Pipe Class A
Nipples | 1/2 - 1 1/2 | All in accordance with Pipe Class A
Swages | 1/2 - 1 1/2 | All in accordance with Pipe Class A
Tubing | 1/2 (O.D.) | Seamless 1.2 mm Wall | A179-CS
| 1 (O.D.) | Seamless 1.6 mm Wall | A179-CS
| 1 (O.D.) | Seamless 2.1 mm Wall | A179-CS
Tube Fittings | 1/2 - 1 | Compression Type, SwageLok or Owner approved equivalent | Steel
|  | 3/4 NPT x 3/4 Tube, S-1210-1-12 | Steel
|  | 3/4 NPT x 1/2 Tube, S-810-1-12 | Steel
|  | 1 NPS x 1 Tube, S-1610-1-16 MPW | Steel
Tube Unions | 1/2 - 1 | Compression Type, SwageLok or Owner approved equivalent | Steel
|  | 1/2 Tube, S-810-6 | Steel
|  | 3/4 Tube, S-1210-6 | Steel
|  | 1 Tube, S-1610-6 | Steel
Valves | GATE
| 3/4 - 1 | All in accordance with Pipe Class A
Steam Trap | 1/2 - 3/4 | Inverted bucket, Armstrong 1811 or Owner approved equivalent | SS | 37
Caption: Class A15 piping components — sizes, descriptions, material codes, and notes
Footnote 37: For high temperature service use thermodynamic (TD) type Spirax - Sarco or Owner approved equivalent.
Extracted from 03-piping-materials-and-line-classes-04 page 21, table 2.