## piping-class-b0-item-sizes-desc
ITEM | Sizes (NPS) | General Description | Material Code | Notes
Pipe | 1/2 – 1 1/2 | Seamless, BE | A106 Gr. B
| 2 – 24 | Seamless, BE | A106 Gr. B | 18
Fittings | 1/2 – 1 1/2 | 3000 SW THF | A105N | 16
| 2 – 24 | Class 300, WT to match pipe | WPB W234 WPB
Nipples | 1/2 – 1 1/2 | Seamless SCH 160 PE/TE | A106 Gr. B
Swages | 1/2 – 2 | Bore to match pipe | A234 WPB
Flanges | 1/2 – 1 1/2 | Class 300 RF THD/SW | A105N | 24
| 2 – 24 | Class 300 RFWN, bore to match pipe | A105N | 2
Bolting | All | Studs | A193 Gr. B7
|  | Nuts | A194 Gr. 2H
Gaskets | All | Class 300 - 3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 – 1 1/2 | Class 800 THD/SW | GA-806/807/808
| 2 – 6, 8 – 24 | Class 300, Flanged | GA-300/301
GLOBE
| 1/2 – 1 1/2 | Class 800 THD/SW | GL-806/807/808
| 2 – 4 | Class 300, Flanged | GL-300
CHECK
| 1/2 – 1 1/2 | Class 800/807/808/809 | CH-805/807/908/809
| 2 – 24 | Class 300 Flanged Swing type | CH-300
| 2 – 24 | Class 300 Flanged Piston Type | CH-305
| 4 – 24 | Class 300, Wafer type | CH-30X
BALL
| 1/2 – 1 1/2 | Class 600 THD | BA-608 | 5
| 2 – 6, 8 – 10 | Class 300 Flanged | BA-300/301
Caption: Piping Class B0 — Item, Sizes, General Description, Material Code, Notes
Extracted from 03-piping-materials-and-line-classes-04 page 22, table 2.