## table-b1s-piping-components
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE | A106 GR. B | 1, 7
| 2 - 24 | Seamless, BE | A106 GR. B | 1
Fittings | 1/2 - 1 1/2 | Class 3000 THD/SW | A105N | 1
| 1/2 - 1 1/2 | Butt weld BW to match pipe | A234 WPB | 1, 7
| 2 - 24 | Butt weld BW to match pipe | A234 WPB | 1
Nipples | 1/2 - 1 1/2 | Seamless SCH xxH PE/TE | A106 GR. B | 1, 7
Flanges | 1/2 - 2 | Bore to match pipe | A234 WPB | 1, 7
| 1/2 - 1 1/2 | Bore to match pipe | A105N | 1, 7, 24
| 2 - 24 | Class 300 RFWN, bore to match pipe | A105N | 1
Bolting | All | Studs | A193 GR. B7M | 1
|  | Nuts | A194 GR. 2HM | 1
Gaskets | All | Class 300 - 3 mm (1/8") THK, "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS | 10
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA-815/817/818 | 7
| 1/2 - 1 1/2 | Class 300 Flanged | GA-310 | 10
| 2 - 6, 8 - 24 | Class 300 Flanged | GA-310/311
GLOBE
| 3/4 - 1 1/2 | Class 800 THD/SW | GL-815/817/818 | 7
| 2 - 6 | Class 300 Flanged | GL-310
CHECK
| 3/4 - 1 1/2 | Class 800 THD/SW | CH-815/817/818/819 | 7
| 1/2 - 24 | Class 300 Flanged | CH-310
| 4 - 24 | Class 300 Flanged | CH-31X
BALL
| 1/2 - 1 1/2 | Class 600 THD | BA-618 | 5, 7
| 2 - 24 | Class 300 Flanged | BA-310/311
Caption: Table B1S — Piping components, sizes, materials, and notes
Extracted from 03-piping-materials-and-line-classes-04 page 25, table 2.