## piping-class-b2-component-sched
ITEM | Sizes (NPS) | General Description | Material Code | Notes
Pipe | 1/2 - 1 | Seamless, PE | A106 GR.B | 9
| 2 - 10 | Seamless, BE | A106 GR.B | 3, 8, 9
| 12 - 24 | Seamless, BE | A106 GR.B | 3, 8, 9
Fittings | 1/2 - 4 | Class 3000 SW/THD | A105N | 9, 16
| 5 - 24 | Butt Weld; WT to match pipe | A234 WPB | 9
Nipples | 1/2 - 4 | Use pipe | A106 GR.B | 9
Swages | 1/2 - 4 | Bore to match pipe | A234 WPB | 9
Flanges | 1/2 - 4 | Class 300 RF THD/SW, bore to match pipe | A105N | 9, 24
| 2 - 24 | Class 300 RF/WN, bore to match pipe | A105N | 2, 9
Bolting | All | Stude | A193 GR.B7 | 9
|  | Nuts | A194 GR.2H | 9
Gaskets | All | Class 300 - 3 mm (1/8) THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves - GATE | 1/2 - 4 | Class 800 THD/SW | GA-806/807/808
| 2 - 6, 8 - 24 | Class 300 Flanged | GA-300/301
Valves - GLOBE | 3/4 - 4 | Class 800 THD/SW | GL-806/807/808
| 2 - 4 | Class 300 Flanged | GL-300
Valves - CHECK | 3/4 - 2 | Class 800 THD Lift type | CH-806/807/808/809
| 3/4 - 24 | Class 300 Flanged Swing type | CH-300 | 6
| 24 | Class 300 Wafer type | CH-30X
Valves - BALL | 1/2 - 4 | Class 600 THD | BA-600 | 5
| 2 - 6, 8 - 18 | Class 300 Flanged | BA-300/301 | 5, 6
Size | 1/2 | 3/4 | 1 | 1 1/2 | 2 | 3 | 4 | 5 | 6 | 8 | 10 | 12 | 14 | 16 | 20 | 22 | 24
W.T. | 160 | 160 | 160 | 160 | 80/40 | 40/std | 40/std | 40/std | 40/std | 20 | 30 | 30/std | Calculate
Caption: Piping Class B2 — Component Schedule
Extracted from 03-piping-materials-and-line-classes-04 page 26, table 2.