## class-b3-line-class-detail
CODE Z662 | CLASS B3
Service | Sour Gas and Hydrocarbon Liquids (Pipelines CSA Z662 Surface Piping)
Maximum Pressure Rating | Lower of ANSI B16.5 Class 300 Material Group 1.1 or CSA Z245.12 PN 50
Temperature Range | -29°C to 120°C
Minimum Corrosion Allowance | 3.0 mm
Radiography | 100%
Post Weld Heat Treatment | All Welds (Note 11)
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, PE | Z245.1 Gr. 241 Cat 1 SS | 1, 3, 7, 9, 14
| 2 - 24 | Seamless, BE | Z245.1 Gr. 241 Cat 1 SS | 1, 3, 8, 9, 14
Fittings | 1/2 - 1 1/2 | Class 3000 THD, (SW as required) | Z245.11 Gr. 241 Cat 1 SS | 1, 7, 9, 14
| 2 - 24 | Class 300 BW, to match pipe | Z245.11 Gr. 241 Cat 1 SS | 1, 9, 14
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 Minimum | Z245.1 Gr. 241 Cat 1 SS | 1, 7, 9, 14
Swages | 1/2 - 1 1/2 | Seamless, to match pipe | Z245.11 Gr. 241 Cat 1 SS | 1, 7, 9, 14
Flanges | 1/2 - 1 1/2 | Class 300 RF THD/SW, bore to match pipe | Z245.12 Gr. 241 Cat 1 SS | 1, 7, 9, 14, 24
| 2 - 24 | Class 300 RFWN, bore to match pipe | Z245.12 Gr. 241 Cat 1 SS | 1, 9, 14, 24
Bolting | All | Studs | A193 GR. B7M | 1
| All | Nuts | A194 GR. 2HM | 1
Gaskets | All | Class 300 - 3 mm (1/8") THK. "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 600 THD/SW | GA-816/817/818 | 7, 32
| 1/2 - 1 1/2 | Class 300 Flanged | GA-310 | 10, 32
| 2 - 6, 8 - 24 | Class 300 Flanged | GA-310/311 | 32
GLOBE
| 3/4 - 1 1/2 | Class 800 THD/SW | GL-815/817/819 | 7, 32
| 2 - 4 | Class 300 Flanged | GL-310 | 32
CHECK
| 3/4 - 1 1/2 | Class 800 THD Lift type | CH-816/817/818/819 | 7, 32
| 2 - 4 | Class 300 Flanged Swing type | CH-310 | 7, 32
| 8 - 24 | Class 300 Wafer Type | CH-31X | 32
BALL
| 1/2 - 1 1/2 | Class 600 THD | BA-618 | 5, 7, 32
| 2 - 6, 8 - 24 | Class 300 Flanged | BA-310/311 | 5, 6, 32
Caption: Code Z662 — Class B3 Piping Material Line Class Detail
Extracted from 03-piping-materials-and-line-classes-04 page 27, table 1.