## piping-class-b5g-component-spec
CODE CSA Z662 | CLASS B5G
Service | Sour Gas - (Pipelines CSA Z662, Surface Piping)
Maximum Pressure Rating | Lower of ANSI B16.5 Class 300 Material Group 1.1 or CSA Z245.12 PN 50
Temperature Range | -45°C to 120°C
Minimum Corrosion Allowance | 3.0 mm
Radiography | 100%
Post Weld Heat Treatment | All Welds (Note 11)
ITEMS | (NPS) | General Description | Material Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, PE | CSA Z245.1 Gr. 241 Cat II (M45C) SS | 1, 7, 9, 33
| 2 – 24 | Seamless, BE | CSA Z245.1 Gr. 241 Cat II (M45C) SS | 1, 3, 8, 9, 33
Fittings | 1/2 - 1 1/2 | Class 3000 THD/SW | CSA Z245.11 Gr. 241 Cat II (M45C) SS | 1, 7, 9, 33
| 2 – 24 | Butt Weld (BW), bore to match pipe | CSA Z245.11 Gr. 241 Cat II (M45C) SS | 1, 3, 8, 9, 33
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 Minimum TE/PE | CSA Z245.1 Gr. 241 Cat II (M45C) SS | 1, 7, 9, 33
Swages | 1/2 - 1 1/2 | Bore to match pipe | CSA Z245.11 Gr. 241 Cat II (M45C) SS | 1, 7, 9, 33
Flanges | 1/2 - 1 1/2 | Class 300 RF THD/SW | CSA Z245.12 Gr. 241 Cat II (M45C) SS | 1, 7, 9, 24, 33
| 2 – 24 | Class 300 RFWN, bore to match pipe | CSA Z245.12 Gr. 241 Cat II (M45C) SS | 1, 3, 8, 9, 33
Bolting | All | Studs | A193 GR. B7M | 1
|  | Nuts | A194 GR. 2HM | 1
Gaskets | All | Class 300 - 3 mm (1/8") THK "Flexitalic, Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA-846/847/848 | 7, 32
| 2 – 6, 8 – 24 | Class 300 RF Flanged | GA 340/341 | 32
GLOBE
| 1/2 - 1 1/2 | Class 800 THD/SW | GL-846/847/848 | 7, 32
| 2 - 4 | Class 300 RF Flanged | GL-340 | 32
CHECK
| 1/2 - 1 1/2 | Class 800 RF THD/SW | CH-846/847/848 | 7, 32
| 2 – 24 | Class 300 RF Flanged Swing type | CH-340 | 32
| 2 – 4 | Class 300 RF Water type | CH-34X | 32
BALL
| 1/2 - 1 1/2 | Class 600 THD | BA-848 | 7, 32
| 2 – 6, 8 – 24 | Class 300 RF Flanged | BA-340/341 | 6, 32
Caption: Piping Class B5G — Component Specification Table
Extracted from 03-piping-materials-and-line-classes-04 page 30, table 1.