## piping-class-b6-component-mater
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE | A333 GR. 6
| 2 - 24 | Seamless, BE | A333 GR. 6 | 3, 8, 9
Fittings | 1/2 - 1 1/2 | Class 3000 THD/SW as required | A420 WPL 6 CL1 | 9
| 2 - 24 | Class 600, WT to match pipe | A420 WPL 6 | 9
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 THD | A333 GR. 6 | 9
Flanges | 1/2 - 24 | Bore to match pipe | A420 WPL 6 | 9
| 1/2 - 1 1/2 | Class 300 RF THD/SW, bore to match pipe | A350 LF 2 CL1 | 3, 24
| 2 - 24 | Class 300 RFWN, bore to match pipe | A350 LF 2 CL1 | 2, 9
Bolting | All | Studs | A193 GR. B7
| All | Nuts | A194 GR. 2H
Gaskets | All | Class 300 - 5 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA-636/637/838
| 2 - 6, 8 - 24 | Class 300 RF Flanged | GA-330/331
GLOBE
| 1/2 - 1 1/2 | Class 800 THD/SW | GL-636/637/835
| 2 - 4 | Class 300 RF Flanged | GL-330
CHECK
| 1/2 - 1 1/2 | Class 800 THD/SW | CH-636/637/838
| 2 - 24 | Class 300 RF Flanged Swing type | CH-330 | 6
| 4 - 24 | Class 300 RF Water type | CH-331
BALL
| 3/4 - 1 1/2 | Class 600 THD | BA-636
| 2 - 6, 8 - 24 | Class 300 RF Flanged | BA-330/331 | 6
Caption: Piping Class B6 — Component Material and Notes
Extracted from 03-piping-materials-and-line-classes-04 page 31, table 1.