## piping-class-b7b-material-line-
CODE B31.3 | CLASS B7B
Service | Sweet Gas, Refrigerants, Ethane, Butane, Propane
Maximum Pressure Rating | Per ANSI B16.5 Class 300 Material Group 1.1
Temperature Range | -100°C to 145°C
Minimum Corrosion Allowance | 0 mm
Radiography | 10% (Note 4)
Post Weld Heat Treatment | Per B31.3
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE | A333 GR. 6
| 2 – 24 | Seamless, BE | A333 GR. 3
Fittings | 1/2 - 1 1/2 | Class 3000 THD/SW | A350 LF 2
| 2 – 24 | BW, WT to match pipe | A420 WPL 3
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 TE/PE | A333 GR. 3
Flanges | 1/2 - 2 | Bore to match pipe | A420 WPL 3
| 1/2 - 1 1/2 | Class 300 RF THD/SW | A350 LF 3 | 24
| 2 – 24 | Class 300 RFWN, bore to match pipe | A350 LF 3 | 2
Bolting | All | Studs | A320 GR. L7
|  | Nuts | A194 GR. 7
Gaskets | All | Class 300 – 3 mm (1/8") THK. "Flexitallic Style CG (API 601) or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA-876/877/878
| 2 – 24 | Class 300 Flanged | GA-370/371
GLOBE
| 1/2 - 1 1/2 | Class 800 THD/SW | GL-876/877/878
| 2 – 4 | Class 800 Flanged | GL-370
CHECK
| 1/2 - 1 1/2 | Class 800 THD/SW | CH-876/877/878/879
| 2 - 24 | Class 300 Flanged | CH-370
| 2 – 24 | Class 300 Wafer type | CH-37X
BALL
| 1/2 - 1 1/2 | Class 800 THD | BA-676/677/678 | 5
| 2 – 6, 8 - 24 | Class 300 Flanged | BA-370/371 | 5
Size | 1/2 | 3/4 | 1 | 1 1/2 | 2 | 3 | 4 | 6 | 8 | 10 | 12 | 14 | 16 | 18 | 20 | 22 | 24
W.T. | 80/xl |  | 40/std | 40/std | 40/std | 40/std | 40/std | 20 | 30 | 20 | 30/std | [5 empty] | Calculate
Caption: Piping Class B7B — Material Line Class Detail
Extracted from 03-piping-materials-and-line-classes-04 page 33, table 1.