## piping-class-b7c-component-sche
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE | A312 TP 304 L
| 2 - 24 | Seamless, BE | A312 TP 304 L
Fittings | 1/2 - 1 1/2 | Class 3000 THD/SW | A403 WP 304 L
| 2 - 24 | Class 300 BW, bore to match pipe | A403 WP 304 L
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 THD/PE | A312 TP 304 L
Swages | 1/2 - 2 | Bore to match pipe | A403 WP 304 L
Flanges | 1/2 - 1 1/2 | Class 300 RF, THD/SW | A182 F 304 L | 24
| 2 - 24 | Class 300 RFWN, bore to match pipe | A182 F 304 L | 25
Bolting | All | Studs Strain Hardened | A193 GR B8 CL2
|  | Nuts | A194 GR 8
Gaskets | All | Class 300 - 3 mm (1/8") THK "Flexitallic" Style CG (API 601) or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA 886/887/888
| 2 - 24 | Class 300 Flanged | GA 380/381
GLOBE
| 1/2 - 1 1/2 | Class 800 THD/SW | GL 886/887/888
| 2 - 4 | Class 300 Flanged | GL 380
CHECK
| 1/2 - 1 1/2 | Class 800 THD/SW | CH 886/887/888/989
| 2 - 24 | Class 300 Flanged | CH 380/382
| 2 - 24 | Class 300 Wafer type | CH 306
BALL
| 1/2 - 1 1/2 | Class 600 THD | BA-688 | 5
| 2 - 24 | Class 300 Flanged | BA-380/381 | 5
Caption: Piping Class B7C — Component Schedule
Extracted from 03-piping-materials-and-line-classes-04 page 34, table 2.