## class-c0-piping-items-table
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 – 1 1/2 | Seamless, BE | A106 GR. B
| 2 – 24 | Seamless, BE | A106 GR. B
Fittings | 1/2 – 1 1/2 | Class 3000 THD/SW | A105 | 16
| 2 – 24 | Class 3000, WF, to match pipe | A234 WPB
Nipples | 1/2 – 1 1/2 | Seamless SCH 160, PE/TE | A106 GR. B
Flanges | 1/2 – 2 | Bore to match pipe | A234 WPB
| 1/2 – 1 1/2 | Class 600 RF THD (SW as required) | A105N | 24
| 2 – 24 | Class 600 RFWN, bore to match pipe | A105N | 2
Bolting | All | Studs | A193 GR. B7
| All | Nuts | A194 GR. 2H
Gaskets | All | Class 600 – 3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 – 1 1/2 | Class 800 THD/SW | GA-806/807/808
| 2 – 6, 8 – 24 | Class 600 Flanged | GA-600/601
GLOBE
| 3/4 – 1 1/2 | Class 800 THD/SW | GL-806/807/808
| 2 – 4 | Class 600 Flanged | GL-600
CHECK
| 1/2 – 1 1/2 | Class 800 THD/SW, Horizontal Lift Type | CH-806/807/808/809
| 2 – 24 | Class 600 Flanged, Swing type | CH-600
| 2 – 24 | Class 600 Wafer type | CH-601
BALL
| 3/4 – 1 1/2 | Class 600 THD | BA-608 | 5
| 2 – 4, 6 – 24 | Class 600 RF Flanged | BA-600/601 | 5
Caption: Piping items, sizes, materials, and notes for CLASS C0
Extracted from 03-piping-materials-and-line-classes-04 page 36, table 2.