## piping-class-c1-materials-table
CODE B31.3 | CLASS C1
Service | Sour Gas and Hydrocarbon Liquids, Rich Amine or Rich Sulfinol (Note 20)
Maximum Pressure Rating | Per ANSI B16.5 Class 600 Material Group 1.1
Temperature Range | -29°C to 204°C
Minimum Corrosion Allowance | 1.5 mm
Radiography | 100%
Post Weld Heat Treatment | All Welds (Note 11)
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, PE | A106 GR. B | 1, 7
| 2 – 24 | Seamless, BE | A106 GR. B | 1
Fittings | 1/2 - 1 1/2 | Class 3000 SW/Class 6000 THD | A105N | 1, 7
| 2 – 24 | Butt Weld, WT to match pipe | A234 WPB | 1
Nipples | 1/2 - 1 1/2 | Seamless xxH THD Ends | A106 GR. B | 1, 7
Swages | 2 – 2 | Bore to match pipe | A234 WPB | 1, 7
Flanges | 1/2 - 1 1/2 | Class 600 RF SW/THD | A105N | 1, 7, 24
| 2 – 24 | Class 600 RFWN, bore to match pipe | A105N | 1, 2
Bolting | All | Studs | A193 GR. B7M | 1
|  | Nuts | A194 GR. 2HM | 1
Gaskets | All | Class 600 - 3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA-816/817/818 | 7
| 1/2 - 1 1/2 | Class 600 Flanged | GA-610 | 10
| 2 – 6, 8 – 24 | Class 600 Flanged | GA-610/611
GLOBE
| 3/4 - 1 1/2 | Class 800 THD/SW | GL-816/817/818 | 7
| 2 – 4 | Class 600 Flanged | GL-610
CHECK
| 1/2 - 1 1/2 | Class 800 THD/SW | CH-816/817/816/819 | 7
| 2 – 24 | Class 600 Flanged, Swing type | CH-610
| 2 – 24 | Class 600 Wafer type | CH-61X
BALL
| 1/2 - 1 1/2 | Class 600 THD | BA-618 | 7
| 1/2 - 1 1/2 | Class 600 Flanged | BA-610 | 10
| 2 – 6, 8 – 24 | Class 600 Flanged | BA-610/611
Caption: CODE B31.3 CLASS C1 — Piping materials and general descriptions for Sour Gas and Hydrocarbon Liquids, Rich Amine or Rich Sulfinol service
Extracted from 03-piping-materials-and-line-classes-04 page 37, table 1.