## class-c1c-piping-component-sche
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE | A333 GR. 6 | 1, 7
| 2 - 24 | Seamless, BE | A333 GR. 6 | 1
Fittings | 1/2 - 1 1/2 | Class 6000 THD/SW | A420 LF 2 CL1 | 7
| 2 - 24 | Butt Weld, W/F to match pipe | A420 WPL 6 | 7
Nipples | 1/2 - 1 1/2 | Seamless xxH TE/PE | A333 GR. 6 | 1, 7
Flanges | 1/2 - 2 | Bore to match pipe | A350 WPL S | 7
| 1/2 - 1 1/2 | Class 600 RF SW/THD | A350 LF 2 CL1 | 1, 7, 24
| 2 - 24 | Class 600 RFWN, bore to match pipe | A350 LF 2 CL1 | 2
Bolting | All | Studs | A193 GR. B7M | 1
|  | Nuts | A194 GR. 2HM | 1
Gaskets | All | Class 600 - 3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves — GATE | 1/2 - 1 1/2 | Class 600 THD/SW | GA-846/847/848 | 7
| 1/2 - 1 1/2 | Class 600 Flanged | GA-640 | 10
| 2 - 6, 8 - 24 | Class 600 Flanged | GA-640/641
Valves — GLOBE | 1/2 - 1 1/2 | Class 600 THD/SW | GL-846/847/848 | 7
| 2 - 4 | Class 600 Flanged | GL-640
Valves — CHECK | 1/2 - 1 1/2 | Class 600 THD/SW | CH-846/847/848/849 | 7
| 2 - 24 | Class 600 Flanged Swing type | CH-640
| 4 - 24 | Class 600 Water type | CH-64X
Valves — BALL | 1/2 - 1 1/2 | Class 600 THD | BA-648 | 7
| 1/2 - 1 1/2 | Class 600 Flanged | BA-640
| 2 - 6, 4 - 24 | Class 600 Flanged | BA-640/641
Caption: CLASS C1C — Piping Component Schedule
Extracted from 03-piping-materials-and-line-classes-04 page 38, table 2.