## class-c2-piping-class-detail-se
CODE Z662 | CLASS C2
Service | Sweet Gas and Hydrocarbon Liquids, Fresh Water (Pipelines CSA Z662 Surface Piping)
Maximum Pressure Rating | Lower of ANSI B16.5 Class 600 Material Group 1.1 or Z245.12 PN 100
Temperature Range | -29°C to 120°C
Minimum Corrosion Allowance | 3 mm
Radiography | 15% (Note 4)
Post Weld Heat Treatment | Per Z662
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 2 | Seamless, PE | A106 GR. B | 9
| 2 - 24 | Seamless, BE | A106 GR. B | 3, 8, 9
Fittings | 1/2 - 2 | Class 3000 THD/SW - | A105N | 9
| 2 - 24 | Butt Weld, WT to match pipe | A234 WPB | 9
Nipples | 1/2 - 2 | Use Pipe | A106 GR. B | 9
Swages | 1/2 - 2 | Bore to match pipe | A234 WPB | 9
Flanges | 1/2 - 2 | Class 600 RF THD/SW | A105N | 9, 24
| 2 - 24 | Class 600 RFWN, bore to match pipe | A105N | 2, 9
Bolting | All | Studs | A193 GR. B7 | 9
|  | Nuts | A194 GR. 2H
Gaskets | All | Class 600 - 3 mm (1/8") THK "Flextallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves: | GATE
| 1/2 - 2 | Class 800 THD/SW | GA-806/807/808
| 2 - 6 - 8 - 24 | Class 600 Flanged | GA-600/601 | 6
GLOBE
| 1/2 - 2 | Class 800 THD/SW | GL-806/807/808
| 2 - 4 | Class 600 Flanged | GL-600
CHECK
| 1/2 - 2 | Class 800 THD/SW | CH-806/807/808/809
| 2 - 24 | Class 600 Flanged Swing type | CH-600 | 6
| 4 - 24 | Class 600 Water type | CH-60X
BALL
| 1/2 - 2 | Class 600 THD | BA-608 | 5
| 2 - 4 - 6 - 24 | Class 600 RF Flanged | BA-600/601 | 5, 6
Caption: CLASS C2 Piping Class Detail — Service, Ratings, and Component Specifications
Extracted from 03-piping-materials-and-line-classes-04 page 40, table 1.