## piping-class-c6-item-details
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, PE | A333 GR. 6
| 2 - 24 | Seamless, BE | A333 GR. 6 | 3, 8, 9
Fittings | 1/2 - 1 1/2 | Class 3000 SW,T | A350 LF2 CL1 | 9
| 2 - 24 | Butt Weld, WT to match pipe | A420 WPL6 | 9
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 TE/PE | A333 GR. 6 | 9
Swages | 1/2 - 2 | Bore to match pipe | A333 WPL 6
Flanges | 1/2 - 1 1/2 | Class 600 RF SW/THD, bore to match pipe | A350 LF2 CL1 | 9, 24
| 2 - 24 | Class 600 RFWN, bore to match pipe | A350 LF 2 CL1 | 2, 9
Bolting | All | Studs | A193 GR. B7
|  | Nuts | A194 GR. 2H
Gaskets | All | Class 600 - 3 mm (1/8") THK. Flexitallic Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 800 THD/SW | GA-836/837/838
| 2 - 6, 8 - 24 | Class 600 RF Flanged | GA-630/631 | 6
GLOBE
| 1/2 - 1 1/2 | Class 800 THD/SW | GL-836/837/838
| 2 - 4 | Class 600 RF Flanged | GL-630
CHECK
| 1/2 - 1 1/2 | Class 800 THD/SW | CH-836/837/838/839
| 2 - 24 | Class 600 RF Flanged Swing type | CH-630 | 6
| 2 - 24 | Class 600 RF Wafer type | CH-63X
BALL
| 1/2 - 1 1/2 | Class 800 THD | BA-636
| 2 - 4, 6 - 16 | Class 600 RF Flanged | BA-630/631 | 6
Caption: Piping Class C6 Item Details
Extracted from 03-piping-materials-and-line-classes-04 page 45, table 2.