## c7b-service-general-properties
CODE B31.3 | CLASS C7B
Service | Sweet Gas, Refrigerants, Ethane, Butane, Propane
Maximum Pressure Rating | Per ANSI B16.5 Class 600 Material Group 1.1
Temperature Range | -100°C to 149°C
Minimum Corrosion Allowance | 0 mm
Radiography | 10% (Note 4)
Post Weld Heat Treatment | Per B31.3
Caption: Piping Class C7B — Service and General Properties
Extracted from 03-piping-materials-and-line-classes-04 page 47, table 1.