## piping-class-c7c-items
ITEM | SIZES (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE | A312 TP 304 L
| 2 - 24 | Seamless, BE | A312 TP 304 L
Fittings | 1/2 - 1 1/2 | Class 3000 THD/SW | A182 F 304 L
| 2 - 24 | Butt Weld, WT to match pipe | A403 WP 304 L
Nipples | 1/2 - 1 1/2 | Seamless 3/4 x 100 THD Ends | A403 WP 304 L
Swages | 1/2 - 2 | Bore to match pipe | A403 WP 304 L
Flanges | 1/2 - 1 1/2 | Class 600 RF THD/SW | A182 F 304 L | 24
| 2 - 24 | Class 600 RFWN, bore to match pipe | A182 F 304 L | 25
Bolting | All | Studs Stainless Hardened | A193 GR. B8 CL2
|  | Nuts | A194 GR. 8
Gaskets | All | Class 600 - 3 mm (1/8") THK "Flexitallic" Style CG (API 601) or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 600 THD/SW | GA-886/887/888
| 2 - 24 | Class 600 Flanged | GA-880/681
GLOBE
| 1/2 - 1 1/2 | Class 600 THD/SW | GL 886/887/888
| 2 - 4 | Class 600 RF Flanged | GL-680
CHECK
| 1/2 - 1 1/2 | Class 800 THD/SW | CH-886/887/888/889
| 2 & Up | Class 600 Flanged Swing type | CH-685
| 6 & Up | Class 600 Water type | CH-6XX
BALL
| 1/2 - 1 1/2 | Class 600 THD | BA-686
| 2 - 24 | Class 600 Flanged | BA-690/681
Caption: Piping Class C7C — Item, Sizes, General Description, Material/Code, Notes
Extracted from 03-piping-materials-and-line-classes-04 page 48, table 1.