## class-d0-piping-material-line-c
CODE B31.3 | CLASS D0
Service | Sweet Gas and Hydrocarbon Liquids, Steam, Boiler Feed Water (Note 29)
Maximum Pressure Rating | Per ANSI B16.5 Class 900 Material Group 1.1
Temperature Range | -29°C to 204°C
Minimum Corrosion Allowance | 0 mm
Radiography | 10% (Note 4)
Post Weld Heat Treatment | Per B31.3
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, BE | A106 GR. B
| 2 - 24 | Seamless, BE | A106 GR. B
Fittings | 1/2 - 1 1/2 | Class 6000 THD/SW | A105M
| 2 - 24 | Butt Weld, WT to match pipe | A234 WPB
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 TE/PE | A106 GR. B
Swages | 1/2 - 2 | Born to match pipe | A234 WPB
Flanges | 1/2 - 1 1/2 | Class 1500 RF THD/SW | A105M | 24
|  | Class 1500 RFWN, bore to match pipe | A105M
| 3 - 4 | Class 900 RFWN, bore to match pipe | A105M
| 6 - 24 | Class 900 RFWN or RTJWN, bore to match pipe | A234 WPB | 2
Bolting | All | Studs | A193 GR. B7
|  | Nuts | A194 GR. 2H
Gaskets | All | Class 900 – 3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 1500 THD/SW | GA-1506/1507/1508
| 2 | Class 1500 Flanged | GA-1500
| 2, 4, 6 - 24 | Class 900 Flanged | GA-900/901/903
GLOBE
| 1/2 - 1 1/2 | Class 1500 THD/SW | GL-1506/1507/1508
| 2 | Class 1500 Flanged | GL-1500
| 1/2 - 12 | Class 900 Flanged | GL-900
CHECK
| 1/2 - 1 1/2 | Class 1500 THD/SW | CH-1506/1507/1508/1509
| 2 | Class 1500 Flanged Swing type | CH-1500
| 4 - 24 | Class 900 Flanged Swing type | CH-900
| 4 - 24 | Class 900 Wafer type | CH-90X
BALL
| 1/2 - 1 1/2 | Class 1500 THD | BA-1506
| 2 | Class 1500 Flanged | BA-1500
| 3 - 4, 6 - 24 | Class 900 Flanged | BA-900/901/903
Caption: Class D0 Piping Material Line Class Detail
Extracted from 03-piping-materials-and-line-classes-04 page 50, table 1.