## piping-class-d2-item-specificat
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 - 1 1/2 | Seamless, PE | A106 GR. B | 3, 9
| 2 - 24 | Seamless, PE | A106 GR. B | 3, 18
Fittings | 1/2 - 1 1/2 | Class 600 THD/SW | A105N | 9
| 2 - 24 | Butt Weld, WT to match pipe | A234 WPB | 9
Nipples | 1/2 - 1 1/2 | Seamless SCH 160 THD Ends | A106 GR. B | 9
Swages | 1/2 - 2 | Bore to match pipe | A234 WPB | 9
Flanges | 1/2 - 1 1/2 | Class 1500 RF THD/SW, bore to match pipe | A105N | 2, 24
| 2 | Class 1500 RFWN, bore to match pipe | A105N | 9
| 3 - 4 | Class 900 RFWN, bore to match pipe | A105N | 9
| 6 - 24 | Class 900 RFWN or RT.JWN, bore to match pipe | A105N | 2, 9
Bolting | All | Studs | A193 GR. B7 | 9
|  | Nuts | A194 GR. 2H | 9
Gaskets | All | Class 900 – 3 mm (1/8") THK 'Flexitallic' Style CG | 316 SS
Valves | GATE
| 1/2 - 1 1/2 | Class 1500 THD/SW | GA-1506/1507/1508
| 2 | Class 1500 Flanged | GA-1500
| 3 - 6, 8 - 24 | Class 900 Flanged | GA-900/901/903 | 6
GLOBE
| 1/2 - 1 1/2 | Class 1500 THD/SW | GL-1508
| 2 | Class 1500 Flanged | GL-1506
| 3 - 4 | Class 900 Flanged | GL-900
CHECK
| 1/2 - 1 1/2 | Class 1500 THD | CH-1506/1507/1508/1509
| 2 | Class 1500 Flanged Swing type | CH-1500
| 3 - 24 | Class 900 Flanged Swing type | CH-900/903 | 6
| 4 - 24 | Class 900 Wafer type | CH-90X
BALL
| 1/2 - 1 1/2 | Class 1500 THD | BA-1508
| 2 | Class 1500 Flanged | BA-1500
| 3 - 4, 6 - 24 | Class 900 Flanged | BA-900/901/903 | 6
Caption: Piping Class D2 — Item Specifications Table
Extracted from 03-piping-materials-and-line-classes-04 page 54, table 2.