## class-e2-piping-component-mater
ITEM | Sizes (NPS) | General Description | Material Code | Notes
Pipe | 1/2 · 1 1/2 | Seamless, PE | A106 GR. B | 3, 9
| 2 – 24 | Seamless, BE | A106 GR. B | 3, 8, 9
Fittings | 1/2 · 1 1/2 | Class 6000 SW/THD | A105N | 9
| 2 – 24 | Butt Weld, WT to match pipe | A234 WPB | 9
Nipples | 1/2 · 1 1/2 | Seamless SCH 160 TE PE | A106 GR. B | 9
Swagers | 1/2 – 2 | Bore to match pipe | A234 WPB
Flanges | 1/2 · 1 1/2 | Class 1500 RF, bore to match pipe | A105N | 9
| 2 · 4 | Class 1500 RFWN, bore to match pipe | A105N | 9
| 6 – 24 | Class 1500 RFWN or RT,WN, bore to match pipe | A105N | 9
Bolting | All | Studs | A193 GR. B7 | 9
|  | Nuts | A194 GR. 2H | 9
Gaskets | All | Class 1500 – 3 mm (1/8") THK "Flexitallic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
Valves | GATE
| 1/2 · 1 1/2 | Class 1500 SW/THD | GA-1506/1507/1508
| 2 – 3, 4 – 18 | Class 1500 Flanged | GA-1500/1501/1503 | 6
GLOBE
| 1/2 · 1 1/2 | Class 1500 SW/THD | GL-1506/1507/1508
| 2 · 4 | Class 1500 Flanged | GL-1500
CHECK
| 1/2 · 1 1/2 | Class 1500 SW/THD | CH-1506/1507/1508/1509
| 2 - 24 | Class 1500 Flanged Swing type | CH-1500 | 6
| 24 | Class 1500 Wafer type | CH-150X
BALL
| 1/2 · 1 1/2 | Class 1500 THD | BA-1508
| 2 – 3, 4 – 18 | Class 1500 Flanged | BA-1500/1501/1503 | 6
Caption: CLASS E2 — Piping component materials and sizes
Extracted from 03-piping-materials-and-line-classes-04 page 64, table 2.