## piping-class-e7-component-specs
ITEM | Sizes (NPS) | General Description | Material/Code | Notes
Pipe | 1/2 – 1 1/2 | Seamless, BE | A333 GR. 6
| 2 – 24 | Seamless, BE | A333 GR. 6
Fittings | 1/2 – 1 1/2 | Class 6000 SW | A350 LF2 CL.1
| 2 – 24 | BW, WT to match pipe | A420 WPL 6
Nipples | 1/2 – 1 1/2 | Seamless SCH 160 TE/PE | A333 GR. 6
Swages | 1/2 – 2 | Bore to match pipe | A420 WPL 6
Flanges | 1/2 – 1 1/2 | Class 1500 RFSW/THD, bore to match pipe | A350 LF 2 CL1 | 24
| 2 – 4 | Class 1500 RFWN, bore to match pipe | A350 LF 2 CL1
| 6 – 24 | Class 1500 RFWN or RTWN, bore to match pipe | A350 LF 2 CL1 | 2
Bolting | All | Studs | A193 GR. B7
|  | Nuts | A194 GR. 2H
Valves | All | Class 1500 – 3 mm (1/8") THK "Flexitalic" Style CG ASME B16.20 or Owner approved equivalent | 316 SS
GATE
| 1/2 – 1 1/2 | Class 1500 SW/THD | GA-1536/1537/1538
| 2 – 3, 4 – 24 | Class 1500 Flanged | GA-1530/1531/1533
GLOBE
| 3/4 – 1 1/2 | Class 1500 SW/THD | GL-1536/1537/1538
| 3/4 – 3 | Class 1500 Flanged | GL-1530
CHECK
| 1/2 – 1 1/2 | Class 1500 SW/THD | CH-1536/1537/1538/1539
| 1 – 2 | Class 1500 Flanged Piston type | CH-1530
| 3 – 24 | Class 1500 Flanged Swing type | CH-1530
| 24 | Class 1500 Wafer type | CH-153X
BALL
| 1/2 – 1 1/2 | Class 1500 THD | BA-1538
| 2 – 3, 4 – 18 | Class 1500 Flanged | BA-1530/1531/1533
Caption: PIPING CLASS E7 — Component specifications
Footnote 2: Maximum Spectacle Blind size shall be 12NPS.
Footnote 24: If using SW flanges, bore to match pipe.
Extracted from 03-piping-materials-and-line-classes-04 page 69, table 2.