## fig-1400-4-recommendations-auto
Key Factor | Recommendation
Automatic Control Valves | - Valves that are not performing well and that have obvious mechanical defects (such as stem corrosion) should be removed and reconditioned. - Use the valve manufacturer alliance with Fisher-Rosemont to ensure valve quality. - Stem finishes of 4 rms provide the best performance. - Avoid lifting valves by their actuators; instead cradle valves with a non-metallic slings. - Use live-loaded combination packings for VDC control in service where the temperature is less than 450°F. - Use graphite packings and oversized actuators for VDC control for valve in service where the temperature is greater than 450°F.
Caption: Fig. 1400-4 Recommendations for Automatic Control Valves
Extracted from 03-piping-materials-and-line-classes-16 page 9, table 2.