## table-d8-1-contd-design-propert
NOMINAL PIPE SIZE and OUTSIDE DIAMETER (inches) | SCHEDULE NUMBER | WALL THICKNESS (inches) | INSIDE DIAM. (inches) | INSIDE SURFACE AREA (sq ft per ft) | OUTSIDE SURFACE AREA (sq ft per ft) | FLOW AREA (sq in) | Cross-Sectional METAL AREA (sq in) | WEIGHT OF PIPE (lb per ft) | WEIGHT OF WATER (lb per ft) | RADIUS OF GYRATION (inches) | SECTION MODULUS (in³)
20 D = 20.000 | — | .188 | 19.624 | 0.91 | 5.24 | 302.8 | 11.70 | 39.8 | 131.0 | 7.00 | 97.4
| — | .218 | 19.564 | 2.87 | 5.24 | 300.6 | 13.58 | 46.1 | 130.5 | 6.99 | 98.3
| 10 | .250 | 19.500 | 3.00 | 5.24 | 298.6 | 15.51 | 52.7 | 129.5 | 6.99 | 99.3
| — | .312 | 19.376 | 2.13 | 5.24 | 294.8 | 19.38 | 65.8 | 127.8 | 6.98 | 93.8
| 20 ST | .375 | 19.250 | 2.26 | 5.24 | 291.0 | 23.12 | 78.6 | 126.2 | 6.98 | 105.3
| — | .438 | 19.124 | 2.35 | 5.24 | 287.3 | 26.9 | 91.5 | 124.4 | 6.92 | 108.9
| 30 XS | .500 | 19.000 | 2.48 | 5.24 | 283.5 | 30.6 | 104.1 | 122.8 | 6.93 | 143.3
| — | .562 | 18.876 | 2.55 | 5.24 | 279.8 | 34.2 | 116.5 | 121.3 | 6.89 | 113.0
| 40 | .593 | 18.814 | 2.58 | 5.24 | 278.0 | 36.2 | 122.9 | 120.4 | 6.90 | 112.4
| — | .750 | 18.500 | 1.17 | 5.24 | 276.1 | 45.0 | 150.2 | 119.6 | 6.87 | 118.2
| 60 | .812 | 18.376 | 1.23 | 5.24 | 265.2 | 48.9 | 166.4 | 114.9 | 6.78 | 222.7
| — | .875 | 18.250 | 3.02 | 5.24 | 261.6 | 52.6 | 178.7 | 113.4 | 6.77 | 240.0
| — | .906 | 18.188 | 1.39 | 5.24 | 259.8 | 54.3 | 184.6 | 112.5 | 6.78 | 248.3
| 80 | 1.031 | 17.938 | 1.80 | 5.24 | 253.7 | 61.4 | 208.9 | 109.9 | 6.73 | 277.2
| — | 1.280 | 17.440 | 2.70 | 5.14 | 238.8 | 75.3 | 256.1 | 103.5 | 6.77 | 329.5
| 100 | 1.281 | 17.438 | 1.87 | 5.24 | 238.8 | 75.3 | 255.9 | 103.5 | 6.73 | 321.8
| 120 | 1.500 | 17.000 | 1.92 | 5.24 | 227.0 | 87.2 | 296.4 | 98.3 | 6.69 | 364.0
| 140 | 1.750 | 16.500 | 1.22 | 5.24 | 213.8 | 100.3 | 341.1 | 92.6 | 6.41 | 421.7
| — | 1.844 | 16.312 | 2.24 | 5.24 | 209.0 | 105.2 | 356.1 | 90.5 | 6.54 | 425.6
| 160 | 1.969 | 16.062 | 1.67 | 5.24 | 202.7 | 111.0 | 379.1 | 87.8 | 6.87 | 459.8
22 D = 22.000 | — | .218 | 21.564 | 2.09 | 5.76 | 365.2 | 14.92 | 50.7 | 158.2 | 7.69 | 91.8
| ST | .312 | 21.376 | 4.46 | 5.76 | 358.8 | 21.6 | 73.5 | 155.5 | 7.67 | 117.8
| XS | .375 | 21.250 | 4.35 | 5.76 | 354.7 | 25.5 | 88.0 | 153.7 | 7.64 | 131.7
| — | .500 | 21.000 | 3.00 | 5.76 | 346.4 | 34.1 | 115.9 | 150.1 | 7.63 | 164.2
| — | .750 | 20.500 |  | 5.76 | 330.1 | 50.6 | 170.8 | 143.0 | 7.59 | 233.4
| — | 1.000 | 20.000 | 3.62 | 5.76 | 314.2 | 66.5 | 224.1 | 136.2 | 7.50 | 296.4
24 D = 24.000 | — | .218 | 23.564 | 3.28 | 6.28 | 436.1 | 16.29 | 55.4 | 188.8 | 8.39 | 95.1
| — | .250 | 23.500 | 3.89 | 6.28 | 433.7 | 18.65 | 63.4 | 187.8 | 8.37 | 107.3
| — | .312 | 23.376 | 3.25 | 6.28 | 428.7 | 23.5 | 79.1 | 185.8 | 8.37 | 132.7
| 10 ST | .375 | 23.250 | 3.39 | 6.28 | 424.6 | 27.8 | 94.6 | 183.8 | 8.35 | 152.2
| 20 | .500 | 23.000 | 3.77 | 6.28 | 415.5 | 37.1 | 125.5 | 179.9 | 8.32 | 198.9
| — | .562 | 22.876 | 3.44 | 6.28 | 411.0 | 41.6 | 141.3 | 178.1 | 8.31 | 221.3
| 30 | .625 | 22.750 | 3.82 | 6.28 | 406.5 | 46.2 | 157.0 | 176.0 | 8.30 | 242.8
| — | .688 | 22.624 | 4.09 | 6.28 | 402.1 | 50.7 | 172.4 | 174.1 | 8.29 | 264.6
| 40 XS | .750 | 22.500 | 3.54 | 6.28 | 397.6 | 55.4 | 187.2 | 172.2 | 8.29 | 285.1
| — | .812 | 22.376 | 4.27 | 6.28 | 393.2 | 59.9 | 203.5 | 170.4 | 8.29 | 305.8
| 60 | .875 | 22.250 | 4.51 | 6.28 | 388.6 | 64.4 | 218.9 | 168.5 | 8.25 | 327.5
| — | .969 | 22.062 | 4.23 | 6.28 | 382.1 | 71.1 | 241.2 | 165.6 | 8.21 | 360.4
| 80 | 1.531 | 20.938 | 4.02 | 6.28 | 344.3 | 109.1 | 367.4 | 149.1 | 7.95 | 504.3
Caption: TABLE D8-1 (Cont'd) DESIGN PROPERTIES of PIPE
Extracted from 03-piping-materials-and-line-classes-17 page 9, table 1.